## Table from CoreWind
Component | Minor Failure | Repair Time (Minor) | Lead Time (Minor) | Major Failure | Repair Time (Major) | Lead Time (Major) | Replacements | Repair Time (Replacement) | Lead Time (Repair)
Direct Drive Generator | 0.546 | 13 | 0 | 0.03 | 49 | 48 | 0.009 | 244 | 336
Power converter | 0.538 | 14 | 0 | 0.338 | 28 | 48 | 0.077 | 170 | 168
Main shaft | 0.231 | 10 | 0 | 0.026 | 36 | 48 | 0.009 | 144 | 168
power electical system | 0.358 | 10 | 0 | 0.016 | 28 | 48 | 0.002 | 54 | 168
yaw system | 0.162 | 10 | 0 | 0.006 | 40 | 48 | 0.001 | 147 | 168
pitch system | 0.824 | 18 | 0 | 0.179 | 38 | 48 | 0.001 | 75 | 168
blades | 0.456 | 8 | 0 | 0.01 | 42 | 48 | 0.001 | 864 | 336
pumps of active ballast system | 0.01 |  | 0
mooring line | 0 |  |  | 0.015 | 240 | 336 | 0.0125 | 360 | 336
anchor |  |  |  | 0.015 | 240 | 336 | 0.0125 | 360 | 336
marine growth removal | 0.12 |  |  |  | 40 | 48
dynamic cable |  |  |  | 0.025 | 240 | 336 | 0.016 | 360 | 336
bouyancy modules | [6 empty] | 0.033 | 40 | 168
export cable |  |  |  | 0.02 | 60 | 48
oss corrective maintenance | 0.2 | 12 | 0 | 0.01 | 60 | 48

## Pairing Failure Modes & Effects
Lefftover Failure Modes | Failure Modes (Direct Connections) | Component | Failure Effects (Direct Connections) | Average Minor/Major Failure | Average Major Failure/ Replacement | Minor Failure | Major Failure | Replacements | Leftover Failure Effects | Average of Turbine Replacements
| generator & gearbox | Direct Drive Generator | Incorrect turbine operation | 0.288 | 0.0195 | 0.546 | 0.03 | 0.009 | Vessel or aircraft collision | 0.013625
|  |  | Increased turbine loads/acceleration | 0.288 | 0.0195 | 0.546 | 0.03 | 0.009
|  | Power converter | Reduced power output | 0.438 | 0.2075 | 0.538 | 0.338 | 0.077
| tower structural | Main shaft | Turbine parked | 0.1285 | 0.0175 | 0.231 | 0.026 | 0.009
|  | power electical system |  | 0.187 | 0.009 | 0.358 | 0.016 | 0.002
| turbine controls | yaw system | Excess dynamics | 0.084 | 0.0035 | 0.162 | 0.006 | 0.001
|  | pitch system |  | 0.5015 | 0.09 | 0.824 | 0.179 | 0.001
RNA Structural |  | blades | Falling topside components | 0.233 | 0.0055 | 0.456 | 0.01 | 0.001
| ballast system failure | pumps of active ballast system | Compromised buoyancy/stability | 0.01 | 0.001 | 0.01
Platform (structural) |  |  | Drift off station | 0.01 | 0.001 | 0.01
Platform (watertightness) |  |  | Large hydrostatic offset | 0.01 | 0.001 | 0.01
|  |  | Capsize | 0.01 | 0.001 | 0.01
|  |  | Sink | 0.01 | 0.001 | 0.01
clump weights or floats | chain | mooring line | change in mooring profile | 0.015 | 0.01375 |  | 0.015 | 0.0125 | Mooring-mooring clashing | 0.027311
connectors | synthetic rope |  | excess mooring loads | 0.015 | 0.01375 |  | 0.015 | 0.0125 | Mooring-cable clashing | 0.033968
| wire rope |  | mooring line nonfunctional | 0.015 | 0.01375 |  | 0.015 | 0.0125 | Anchor-cable clashing | 0.033968
|  |  | shared line nonfunctional | 0.015 | 0.01375 |  | 0.015 | 0.0125
| single anchor | anchor | excess anchor load | 0.015 | 0.01375 |  | 0.015 | 0.0125
| shared anchor |  | anchor dragging | 0.015 | 0.01375 |  | 0.015 | 0.0125
|  | marine growth removal |  | 0.12 | 0.012 | 0.12
static cable | dynamic cable | dynamic cable | change in cable profile | 0.025 | 0.0205 |  | 0.025 | 0.016
cable protection system |  |  | excessive load on cable | 0.025 | 0.0205 |  | 0.025 | 0.016
tether and anchor systems |  |  |  | 0.025 | 0.0205 |  | 0.025 | 0.016
terminations |  |  |  | 0.025 | 0.0205 |  | 0.025 | 0.016
| bouyancy modules | bouyancy modules |  | 0.33 | 0.033 |  |  | 0.033
|  | export cable | array cable loss of connectivity | 0.02 | 0.02 |  | 0.02
|  |  | Substation/grid interruption | 0.105 | 0.01 | 0.2 | 0.01
| offshore joints | oss corrective maintenance | Reduced AEP | 0.105 | 0.01 | 0.2 | 0.01

## Conditional Probabilities
|  |  |  | First Failure |  | Second Failure |  | Probability of Second Failure Given First Failure | [6 empty] | Conditional Probabilities
| Name | Probability |  | Name | Probability | Name | Probability | Lower Bound | Higher Bound | Midpoint |  |  |  |  | Name | Probability | Parent Probability | Lower bound | Upper Bound | Midpoint | Name | Probability | Parent Probability | Lower bound | Upper Bound | Midpoint
1 | Incorrect turbine operation | 0.0195 | 0 | Incorrect turbine operation | 0.0195 | Increased turbine loads | 0.0195 | 0.0195 | 1 | 0.50975 |  | 4.1674 | 1 | 0 | Incorrect turbine operation | 0.0195 | 0.0195 | 0.0195 | 1 | 0.50975 | chain | 0.015 | 0.01375 | 0.00020625 | 0.01375 | 9.5949e-05 | 0.9999
2 | Increased turbine loads | 0.0195 | 1 | Incorrect turbine operation | 0.0195 | Turbine parked | 0.0175 | 0.0175 | 0.89744 | 0.45747 |  |  | 2 | 1 | Increased turbine loads | 0.0195 | 0.0195 | 0.0195 | 1 | 0.50975 | wire rope | 0.015 | 0.01375 | 0.00020625 | 0.01375 | 9.5949e-05 | 0.9999
3 | Vessel or Aircraft Collision | 0.013625 | 2 | Incorrect turbine operation | 0.0195 | Reduced power output | 0.2075 | 0.2075 | 1 | 0.60375 |  |  | 3 | 2 | Vessel or Aircraft Collision | 0.013625 | 0.0195 | 0.013625 | 0.69872 | 0.35617 |  | 0.985 | 0.01375 | 0.013544 | 0.01375 | 0.00018764 | 0.99981
4 | Falling topside components | 0.0055 | 3 | Incorrect turbine operation | 0.0195 | RNA structural | 0.233 | 0.233 | 1 | 0.6165 |  |  | 4 | 3 | Falling topside components | 0.0055 | 0.0195 | 0.0055 | 0.28205 | 0.14378
5 | Turbine parked | 0.0175 | 4 | Incorrect turbine operation | 0.0195 | generator & gearbox | 0.288 | 0.288 | 1 | 0.644 |  |  | 5 | 4 | Turbine parked | 0.0175 | 0.0195 | 0.0175 | 0.89744 | 0.45747
6 | Reduced power output | 0.2075 | 5 | Incorrect turbine operation | 0.0195 | turbine controls | 0.54337 | 0.54337 | 1 | 0.77169 |  |  | 6 | 5 | Reduced power output | 0.2075 | 0.0195 | 0.2075 | 1 | 0.60375
7 | Drift off station | 0.001 | 6 | Incorrect turbine operation | 0.0195 | tower structural | 0.1285 | 0.1285 | 1 | 0.56425 |  |  | 7 | 6 | Drift off station | 0.001 | 0.0195 | 0.001 | 0.051282 | 0.026141
8 | Compromised buoyancy/stability | 0.001 | 7 | Increased turbine loads | 0.0195 | Incorrect turbine operation | 0.0195 | 0.0195 | 1 | 0.50975 |  |  | 8 | 7 | Compromised buoyancy/stability | 0.001 | 0.0195 | 0.001 | 0.051282 | 0.026141
9 | Large hydrostatic offset (angle of list/loll or draft change) | 0.001 | 8 | Increased turbine loads | 0.0195 | Reduced power output | 0.2075 | 0.2075 | 1 | 0.60375 |  |  | 9 | 8 | Large hydrostatic offset (angle of list/loll or draft change) | 0.001 | 0.0195 | 0.001 | 0.051282 | 0.026141
10 | Excess dynamics | 0.093185 | 9 | Increased turbine loads | 0.0195 | RNA structural | 0.233 | 0.233 | 1 | 0.6165 |  |  | 10 | 9 | Excess dynamics | 0.093185 | 0.0195 | 0.093185 | 1 | 0.54659
11 | Capsize | 0.001 | 10 | Increased turbine loads | 0.0195 | generator & gearbox | 0.288 | 0.288 | 1 | 0.644 |  |  | 11 | 10 | Capsize | 0.001 | 0.0195 | 0.001 | 0.051282 | 0.026141
12 | Sink | 0.001 | 11 | Increased turbine loads | 0.0195 | turbine controls | 0.54337 | 0.54337 | 1 | 0.77169 |  |  | 12 | 11 | Sink | 0.001 | 0.0195 | 0.001 | 0.051282 | 0.026141
13 | Mooring-mooring clashing | 0.027311 | 12 | Increased turbine loads | 0.0195 | tower structural | 0.1285 | 0.1285 | 1 | 0.56425 |  |  | 13 | 12 | Mooring-mooring clashing | 0.27311 | 0.0195 | 0.27311 | 1 | 0.63655
14 | Mooring-cable clashing | 0.033968 | 13 | Increased turbine loads | 0.0195 | platform (structural integrity) | 0.01 | 0.01 | 0.51282 | 0.26141 |  |  | 14 | 13 | Mooring-cable clashing | 0.033968 | 0.0195 | 0.033968 | 1 | 0.51698
15 | Anchor-cable clashing | 0.033968 | 14 | Vessel or Aircraft Collision | 0.013625 | Falling topside components | 0.0055 | 0.0055 | 0.40367 | 0.20458 |  |  | 15 | 14 | Anchor-cable clashing | 0.033968 | 0.0195 | 0.033968 | 1 | 0.51698
16 | Change in mooring profile | 0.01375 | 15 | Vessel or Aircraft Collision | 0.013625 | Turbine parked | 0.0175 | 0.0175 | 1 | 0.50875 |  |  | 16 | 15 | Change in mooring profile | 0.01375 | 0.0195 | 0.01375 | 0.70513 | 0.35944
17 | Excess mooring loads | 0.01375 | 16 | Vessel or Aircraft Collision | 0.013625 | Reduced power output | 0.2075 | 0.2075 | 1 | 0.60375 |  |  | 17 | 16 | Excess mooring loads | 0.01375 | 0.0195 | 0.01375 | 0.70513 | 0.35944
18 | Mooring line nonfunctional | 0.01375 | 17 | Vessel or Aircraft Collision | 0.013625 | Drift off station | 0.001 | 0.001 | 0.073394 | 0.037197 |  |  | 18 | 17 | Mooring line nonfunctional | 0.01375 | 0.0195 | 0.01375 | 0.70513 | 0.35944
19 | Shared line nonfunctional | 0.01375 | 18 | Vessel or Aircraft Collision | 0.013625 | Large hydrostatic offset (angle of list/loll or draft change) | 0.001 | 0.001 | 0.073394 | 0.037197 |  |  | 19 | 18 | Shared line nonfunctional | 0.01375 | 0.0195 | 0.01375 | 0.70513 | 0.35944
20 | Excess Anchor Loads | 0.01375 | 19 | Vessel or Aircraft Collision | 0.013625 | Excess dynamics | 0.001 | 0.001 | 0.073394 | 0.037197 |  |  | 20 | 19 | Excess Anchor Loads | 0.01375 | 0.0195 | 0.01375 | 0.70513 | 0.35944
21 | Anchor dragging | 0.01375 | 20 | Vessel or Aircraft Collision | 0.013625 | Capsize | 0.093185 | 0.093185 | 1 | 0.54659 |  |  | 21 | 20 | Anchor dragging | 0.01375 | 0.0195 | 0.01375 | 0.70513 | 0.35944
22 | Change in cable profile | 0.0205 | 21 | Vessel or Aircraft Collision | 0.013625 | Substation/grid interruption | 0.01 | 0.01 | 0.73394 | 0.37197 |  |  | 22 | 21 | Change in cable profile | 0.0205 | 0.0195 | 0.0205 | 1 | 0.51025
23 | Excessive load on cable | 0.0205 | 22 | Vessel or Aircraft Collision | 0.013625 | RNA structural | 0.233 | 0.233 | 1 | 0.6165 |  |  | 23 | 22 | Excessive loadg on cable | 0.0205 | 0.0195 | 0.0205 | 1 | 0.51025
24 | Array cable: Loss of connectivity | 0.02 | 23 | Vessel or Aircraft Collision | 0.013625 | generator & gearbox | 0.288 | 0.288 | 1 | 0.644 |  |  | 24 | 23 | Array cable: Loss of connectivity | 0.02 | 0.0195 | 0.02 | 1 | 0.51
25 | Substation/grid interruption | 0.01 | 24 | Vessel or Aircraft Collision | 0.013625 | turbine controls | 0.54337 | 0.54337 | 1 | 0.77169 |  |  | 25 | 24 | Substation/grid interruption | 0.01 | 0.0195 | 0.01 | 0.51282 | 0.26141
26 | Reduced AEP | 0.01 | 25 | Vessel or Aircraft Collision | 0.013625 | tower structural | 0.1285 | 0.1285 | 1 | 0.56425 |  |  | 26 | 25 | Reduced AEP | 0.01 | 0.0195 | 0.01 | 0.51282 | 0.26141
27 | RNA structural | 0.233 | 26 | Vessel or Aircraft Collision | 0.013625 | platform (structural integrity) | 0.01 | 0.01 | 0.73394 | 0.37197 |  |  | 27 | 26 | RNA structural | 0.233 | 0.0195 | 0.233 | 1 | 0.6165
28 | generator & gearbox | 0.288 | 27 | Vessel or Aircraft Collision | 0.013625 | platform (watertightness) | 0.01 | 0.01 | 0.73394 | 0.37197 |  |  | 28 | 27 | generator & gearbox | 0.288 | 0.0195 | 0.288 | 1 | 0.644
29 | turbine controls | 0.54337 | 28 | Vessel or Aircraft Collision | 0.013625 | ballast system failure | 0.01 | 0.01 | 0.73394 | 0.37197 |  |  | 29 | 28 | turbine controls | 0.54337 | 0.0195 | 0.54337 | 1 | 0.77169
30 | tower structural | 0.1285 | 29 | Vessel or Aircraft Collision | 0.013625 | chain | 0.015 | 0.015 | 1 | 0.5075 |  |  | 30 | 29 | tower structural | 0.1285 | 0.0195 | 0.1285 | 1 | 0.56425
31 | platform (structural integrity) | 0.01 | 30 | Vessel or Aircraft Collision | 0.013625 | synthetic rope | 0.015 | 0.015 | 1 | 0.5075 |  |  | 31 | 30 | platform (structural integrity) | 0.01 | 0.0195 | 0.01 | 0.51282 | 0.26141
32 | platform (watertightness) | 0.01 | 31 | Vessel or Aircraft Collision | 0.013625 | wire rope | 0.015 | 0.015 | 1 | 0.5075 |  |  | 32 | 31 | platform (watertightness) | 0.01 | 0.0195 | 0.01 | 0.51282 | 0.26141
33 | ballast system failure | 0.01 | 32 | Vessel or Aircraft Collision | 0.013625 | connectors | 0.015 | 0.015 | 1 | 0.5075 |  |  | 33 | 32 | ballast system failure | 0.01 | 0.0195 | 0.01 | 0.51282 | 0.26141
34 | chain | 0.015 | 33 | Vessel or Aircraft Collision | 0.013625 | clump weights or floats | 0.015 | 0.015 | 1 | 0.5075 |  |  | 34 | 33 | chain | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
35 | synthetic rope | 0.015 | 34 | Vessel or Aircraft Collision | 0.013625 | buoyancy modules | 0.33 | 0.33 | 1 | 0.665 |  |  | 35 | 34 | synthetic rope | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
36 | wire rope | 0.015 | 35 | Vessel or Aircraft Collision | 0.013625 | cable protection system | 0.025 | 0.025 | 1 | 0.5125 |  |  | 36 | 35 | wire rope | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
37 | connectors | 0.015 | 36 | Vessel or Aircraft Collision | 0.013625 | dynamic cable | 0.025 | 0.025 | 1 | 0.5125 |  |  | 37 | 36 | connectors | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
38 | clump weights or floats | 0.015 | 37 | Vessel or Aircraft Collision | 0.013625 | terminations | 0.025 | 0.025 | 1 | 0.5125 |  |  | 38 | 37 | clump weights or floats | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
39 | single anchor | 0.015 | 38 | Falling topside components | 0.0055 | RNA structural | 0.233 | 0.233 | 1 | 0.6165 |  |  | 39 | 38 | single anchor | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
40 | shared anchor | 0.015 | 39 | Falling topside components | 0.0055 | generator & gearbox | 0.288 | 0.288 | 1 | 0.644 |  |  | 40 | 39 | shared anchor | 0.015 | 0.0195 | 0.015 | 0.76923 | 0.39212
41 | buoyancy modules | 0.33 | 40 | Falling topside components | 0.0055 | turbine controls | 0.54337 | 0.54337 | 1 | 0.77169 |  |  | 41 | 40 | buoyancy modules | 0.33 | 0.0195 | 0.33 | 1 | 0.665
42 | tether and anchor systems | 0.025 | 41 | Falling topside components | 0.0055 | tower structural | 0.1285 | 0.1285 | 1 | 0.56425 |  |  | 42 | 41 | tether and anchor systems | 0.025 | 0.0195 | 0.025 | 1 | 0.5125
43 | cable protection system | 0.025 | 42 | Falling topside components | 0.0055 | platform (structural integrity) | 0.01 | 0.01 | 1 | 0.505 |  |  | 43 | 42 | cable protection system | 0.025 | 0.0195 | 0.025 | 1 | 0.5125
44 | dynamic cable | 0.025 | 43 | Falling topside components | 0.0055 | platform (watertightness) | 0.01 | 0.01 | 1 | 0.505 |  |  | 44 | 43 | dynamic cable | 0.025 | 0.0195 | 0.025 | 1 | 0.5125
45 | static cable | 0.025 | 44 | Falling topside components | 0.0055 | ballast system failure | 0.01 | 0.01 | 1 | 0.505 |  |  | 45 | 44 | static cable | 0.025 | 0.0195 | 0.025 | 1 | 0.5125
46 | terminations | 0.025 | 45 | Falling topside components | 0.0055 | chain | 0.015 | 0.015 | 1 | 0.5075 |  |  | 46 | 45 | terminations | 0.025 | 0.0195 | 0.025 | 1 | 0.5125
47 | offshore joints | 0.105 | 46 | Falling topside components | 0.0055 | synthetic rope | 0.015 | 0.015 | 1 | 0.5075 |  |  | 47 | 46 | offshore joints | 1.05 | 0.0195 | 1.05 | 1 | 1.025
|  |  |  | Falling topside components | 0.0055 | wire rope | 0.015 | 0.015 | 1 | 0.5075
| 0.99362 |  |  | Falling topside components | 0.0055 | connectors | 0.015 | 0.015 | 1 | 0.5075
|  |  |  | Falling topside components | 0.0055 | clump weights or floats | 0.015 | 0.015 | 1 | 0.5075
|  |  |  | Falling topside components | 0.0055 | buoyancy modules | 0.33 | 0.33 | 1 | 0.665
|  |  |  | Falling topside components | 0.0055 | cable protection system | 0.025 | 0.025 | 1 | 0.5125
|  |  |  | Falling topside components | 0.0055 | dynamic cable | 0.025 | 0.025 | 1 | 0.5125 | 0.2
|  |  |  | Turbine parked | 0.0175 | Increased turbine loads | 0.0195 | 0.0195 | 1 | 0.50975
|  |  |  | Turbine parked | 0.0175 | Reduced power output | 0.2075 | 0.2075 | 1 | 0.60375
The rest of these calculations are done in Python

## Conditional Probabilities (2)
Incorrect turbine operation 1 | 0.0195
Increased turbine loads/acceleration 1 | 0.0195
Vessel or aircraft collision 1 | 0.013625
Falling topside components 1 | 0.0055 | Name | Probability | Parent Probability | Lower bound | Upper Bound | Midpoint
Turbine parked 1 | 0.0175 | chain | 0 | 0 | 0 | 0 | 0 | 1
Reduced power output 1 | 0.2075 | wire rope | 0 | 0 | 0 | 0 | 0 | 1
Drift off station 1 | 0.001 |  | 1 | 0 | 0 | 0 | 0 | 1
Compromised buoyancy/stability 1 | 0.001
Large hydrostatic offset (angle of list/loll or draft change) 1 | 0.001
Excess dynamics 1 | 0.093185
Capsize 1 | 0.001
Sink 1 | 0.001
Mooring-mooring clashing - 1 | 0.027311
Mooring-cable clashing - 1 | 0.033969
Anchor-cable clashing - 1 | 0.033969
Change in mooring profile - a | 0.01375
Change in mooring profile - b | 0.01375
Excess mooring loads - a | 0.01375
Excess mooring loads - b | 0.01375
Mooring line nonfunctional - a | 0.01375
Mooring line nonfunctional - b | 0.01375
Excess anchor load - a | 0.01375
Excess anchor load - b | 0.01375
Anchor dragging - a | 0.01375
Anchor dragging - b | 0.01375
Array cable: Loss of connectivity 1 | 0.02
RNA structural 1 | 0.233
generator & gearbox 1 | 0.288
turbine controls 1 | 0.54337
tower structural 1 | 0.1285
platform (structural integrity) 1 | 0.01
platform (watertightness) 1 | 0.01
ballast system failure 1 | 0.01
chain 1a | 0.015
chain 1b | 0.015
synthetic rope 1a | 0.015
synthetic rope 1b | 0.015
single anchor 1a | 0.015
single anchor 1b | 0.015
Incorrect turbine operation 2 | 0.0195
Increased turbine loads/acceleration 2 | 0.0195
Vessel or aircraft collision 2 | 0.013625
Falling topside components 2 | 0.0055
Turbine parked 2 | 0.0175
Reduced power output 2 | 0.2075
Drift off station 2 | 0.001
Compromised buoyancy/stability 2 | 0.001
Large hydrostatic offset (angle of list/loll or draft change) 2 | 0.001
Excess dynamics 2 | 0.093185
Capsize 2 | 0.001
Sink 2 | 0.001
Mooring-mooring clashing - 2 | 0.027311
Mooring-cable clashing - 2n | 0.033969
Mooring-cable clashing - 2m | 0.033969
Anchor-cable clashing - 2n | 0.033969
Anchor-cable clashing - 2m | 0.033969
Change in mooring profile - c | 0.01375
Change in mooring profile - d | 0.01375
Excess mooring loads - c | 0.01375
Excess mooring loads - d | 0.01375
Mooring line nonfunctional - c | 0.01375
Mooring line nonfunctional - d | 0.01375
Excess anchor load - c | 0.01375
Excess anchor load - d | 0.01375
Anchor dragging - c | 0.01375
Anchor dragging - d | 0.01375
Array cable: Loss of connectivity 2n | 0.02
Array cable: Loss of connectivity 2m | 0.02
RNA structural 2 | 0.233
generator & gearbox 2 | 0.288
turbine controls 2 | 0.54337
tower structural 2 | 0.1285
platform (structural integrity) 2 | 0.01
platform (watertightness) 2 | 0.01
ballast system failure 2 | 0.01
chain 2c | 0.015
chain 2d | 0.015
synthetic rope 2c | 0.015
synthetic rope 2d | 0.015
single anchor 2c | 0.015
single anchor 2d | 0.015
Shared line nonfunctional - s | 0.01375
Mooring-cable clashing - sn | 0.033969
Change in cable profile - n | 0.0205
Change in cable profile - m | 0.0205
Excessive load on cable - n | 0.0205
Excessive load on cable - m | 0.0205
Substation/grid interruption - B | 0.01
Reduced AEP - B | 0.01
chain - s | 0.015
clump weights or floats - s | 0.015
tether and anchor systems - B | 0.025
cable protection system - B | 0.025
dynamic cable - n | 0.025
dynamic cable - m | 0.025
static cable - m | 0.025
terminations - B | 0.025
offshore joints - B | 0.105