## Sheet1
Failure Mode2 | Failure Cause | Potential End Effects | Occurrence | Severity | Detection | RPN | Mult-Turbine | System | Do you think the failure mode can cause array/farm level failure? IWES | Occurence IWES | Sev1 | Sev2 | Sev3 | Sev4 | Severity IWES | Detection3 IWES | Do you think the failure mode can cause array/farm level failure? -RenewRisk | Occurence -RenewRisk | Sev1-RenewRisk | Sev2-RenewRisk | Sev3-RenewRisk | Sev4-RenewRisk | Severity-RenewRisk | Detection3-RenewRisk | RPN-RenewRisk | Do you think the failure mode can cause array/farm level failure? -UCC | Occurence -UCC | Sev1-UCC | Sev2-UCC | Sev3-UCC | Sev4-UCC | Severity-UCC | Detection3-UCC
Floating Support Structure Capsize | Design | Watertight fault | 2.3333 | 3.6667 | 4.3333 | 40.8333 | 1 | Floating Support Structure | 1 | 4 | 2 | 4 | 4 | 3 | 4 | 5 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 50 | 1 | 1 | 2 | 2 | 5 | 5 | 5 | 3
Floating Support Structure Cracks | Design | Structural failure | 1.3333 | 2.1333 | 2.6667 | 31.8 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 5 | 5 | 5 | 4 | 40 | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 4
Additional Structures Failures | Operation | Potential Failure | 3 | 2.9333 | 3.3333 | 29.6667 | 0.33333 | Floating Support Structure | 0 | 3 | 4 | 2 | 2 | 2 | 4 | 3 | 1 | 3 | 5 | 1 | 2 | 4 | 5 | 4 | 60 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3
Additional Structures Failures | Operation | Potential failure of landing platform | 1 | 2.2667 | 2 | 20.8 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 5 | 3 | 4 | 5 | 5 | 4 | 40 | 0 | 1 | 2 | 1 | 3 | 3 | 3 | 2
Floating Support Structure Watertight fault | Maintenance | Potential Failure | 3 | 3.1333 | 3 | 33.5 | 0.33333 | Floating Support Structure | 0 | 4 | 3 | 3 | 3 | 4 | 4 | 3 | 1 | 2 | 1 | 2 | 4 | 5 | 5 | 2 | 20 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 4
Floater unit sinkage | Design | Potential Failure | 2 | 3.8667 | 3.6667 | 31.2 | 1 | Floating Support Structure | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | 2 | 2 | 4 | 5 | 5 | 5 | 4 | 40 | 1 | 1 | 1 | 2 | 5 | 4 | 5 | 4
Floating Support Structure SStructural plastic deformation | Operation and Maintenance | Local stress accumulation | 2 | 4.2667 | 4.3333 | 33.6 | 0 | Floating Support Structure | 0 | 3 | 2 | 3 | 4 | 4 | 4 | 4 | 0 | 2 | 5 | 4 | 5 | 5 | 5 | 5 | 50 | 0 | 1 | 5 | 3 | 5 | 5 | 5 | 4
Floating Support Structure Watertight fault | Maintenance | Asset damage | 2.3333 | 3.9333 | 3.6667 | 27 | 0 | Floating Support Structure | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 3 | 0 | 2 | 5 | 4 | 5 | 5 | 5 | 5 | 50 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3
Additional Structures Failures | Operation | Potential Failure | 2.3333 | 3.0667 | 3 | 23 | 0.33333 | Floating Support Structure | 0 | 3 | 4 | 2 | 2 | 2 | 4 | 3 | 1 | 2 | 5 | 1 | 2 | 3 | 5 | 4 | 40 | 0 | 2 | 4 | 1 | 4 | 3 | 4 | 2
Floating Support Structure Watertight fault | Environmental condition | Watertight fault | 1.6667 | 2.0667 | 2.3333 | 31.75 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 4 | 5 | 5 | 4 | 40 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3
Additional Structures Failures | Operation | Increased risk of collision, potential damage to the floater | 1.6667 | 1.9333 | 2 | 22.25 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 1 | 2 | 2 | 4 | 3 | 36 | 0 | 2 | 2 | 2 | 4 | 4 | 4 | 3
Floating Support Structure Capsize | Design | Project cancellation | 2 | 3.8667 | 3.6667 | 25.8333 | 1 | Floating Support Structure | 1 | 3 | 3 | 4 | 5 | 4 | 5 | 3 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 50 | 1 | 1 | 2 | 1 | 5 | 5 | 5 | 3
Floating Support Structure Hit by dropped objects | Operation | Asset damage | 0.66667 | 3.1333 | 3.3333 | 26 | 0 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 0 | 1 | 5 | 2 | 5 | 5 | 5 | 5
Additional Structures Failures | Operation | Potential Failure | 1.6667 | 1.2667 | 1.6667 | 19 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 1 | 2 | 2 | 2 | 1 | 6 | 0 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Floating Support Structure Structural break | Operation and Maintenance | Asset damage | 1.6667 | 2.2667 | 2 | 36 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 3 | 5 | 4 | 5 | 3 | 45 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 3
Floating Support Structure Structural break | Operation and Maintenance | Watertight fault | 1.6667 | 2.2667 | 2 | 33.75 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 2 | 3 | 5 | 5 | 5 | 3 | 45 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 3
Floating Support Structure Structural break | Operation | Tower collapse | 1 | 2.9333 | 2.3333 | 25 | 0.66667 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 5 | 4 | 5 | 5 | 5 | 4 | 40 | 1 | 1 | 2 | 3 | 5 | 5 | 5 | 3
Floater unit sinkage | Operation | Potential Failure | 1 | 2.7333 | 2.6667 | 21.25 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 3 | 5 | 5 | 5 | 5 | 50 | 1 | 1 | 4 | 3 | 5 | 5 | 5 | 3
Floating Support Structure Hit by dropped objects | Environmental condition | Asset damage | 1.3333 | 2.4667 | 3 | 27 | 0.66667 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 4 | 4 | 4 | 5 | 40 | 1 | 2 | 3 | 3 | 5 | 5 | 5 | 4
Floating Support Structure Structural break | Design | Watertight fault | 1.3333 | 2.6 | 2.3333 | 30 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 4 | 5 | 5 | 5 | 4 | 40 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 3
Floating Support Structure Structural break | Maintenance | Watertight fault | 1.6667 | 2.6 | 2.3333 | 37.5 | 0.66667 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 4 | 5 | 5 | 5 | 4 | 60 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 3
Floating Support Structure Watertight fault | Manufacturing and Installation | Reduced stability | 1.6667 | 2.1333 | 2.6667 | 32.5 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 5 | 1 | 4 | 4 | 5 | 4 | 40 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 4
Additional Structures Failures | Operation | Potential Failure | 3 | 3.1333 | 4 | 36 | 0.33333 | Floating Support Structure | 0 | 4 | 2 | 4 | 4 | 3 | 4 | 5 | 1 | 3 | 3 | 2 | 4 | 4 | 4 | 2 | 24 | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 5
Floating Support Structure Cracks | Manufacturing | Watertight fault | 2 | 1.8 | 2.3333 | 36 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 1 | 4 | 4 | 4 | 3 | 36 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 4
Floating Support Structure Hit by dropped objects | Operation | Asset damage | 2.6667 | 2.8667 | 4.3333 | 33.4 | 0 | Floating Support Structure | 0 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 0 | 2 | 1 | 2 | 3 | 3 | 3 | 5 | 30 | 0 | 3 | 1 | 2 | 5 | 5 | 5 | 5
Floating Support Structure Structural break | Environmental condition | Structural reassessment | 1 | 2.3333 | 3 | 26.2 | 0.33333 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 5 | 5 | 5 | 4 | 40 | 0 | 1 | 1 | 1 | 5 | 4 | 5 | 5
Additional Structures Failures | Operation | Potential Failure | 1.6667 | 1.8 | 2.6667 | 32.6667 | 0.66667 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 1 | 3 | 4 | 4 | 4 | 48 | 1 | 2 | 1 | 2 | 4 | 3 | 4 | 4
Floating Support Structure Cracks | Installation | Structural failure | 3 | 3.6 | 3.6667 | 41.1667 | 0.66667 | Floating Support Structure | 1 | 3 | 4 | 4 | 5 | 5 | 5 | 5 | 1 | 3 | 1 | 3 | 4 | 5 | 5 | 3 | 45 | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3
Floating Support Structure Capsize | Environmental condition | Asset damage | 1 | 2.4 | 2.6667 | 30 | 0.66667 | Floating Support Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 5 | 5 | 5 | 4 | 40 | 1 | 1 | 2 | 1 | 5 | 4 | 5 | 4
Floating Support Structure Cracks | Operation | Structural failure | 2.6667 | 3.2 | 3.6667 | 39.1667 | 0.66667 | Floating Support Structure | 1 | 3 | 2 | 4 | 4 | 3 | 4 | 3 | 1 | 3 | 1 | 3 | 4 | 5 | 5 | 4 | 60 | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 4
Anchor failure [1], [17] | Operation | Anchor failure | 1.5 | 3 | 4 | 34.8 | 0.5 | Mooring lines | 1 | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 0 | 2 | 1 | 3 | 3 | 4 | 4 | 4
Anchor failure [1], [17] | Operation | Anchor failure | 1.5 | 3 | 4 | 34.8 | 0.5 | Mooring lines | 1 | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 0 | 2 | 1 | 3 | 3 | 4 | 4 | 4
Failure in buoyancy element | Operation |  | 3 | 2.2 | 3.5 | 33.75 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 3 | 3 | 3 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 3
Failure in clump weight | Operation |  | 2.5 | 2.2 | 4 | 33 | 0.5 | Mooring lines | 0 | 2 | 1 | 1 | 3 | 3 | 3 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Fairlead failure [1], [17] | Operation | The anchor cannot be dropped and lift | 3 | 2.2 | 4 | 32 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 3 | 3 | 3 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Fairlead failure [1],[17] | Operation | The anchor cannot be dropped and lift | 3 | 2.2 | 4 | 30 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 3 | 3 | 3 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Monitoring system fails | Operation | Unable to monitor tension in the mooring lines | 2.5 | 1.9 | 3 | 21.25 | 0.5 | Mooring lines | 0 | 2 | 1 | 1 | 3 | 3 | 3 | 4 | 1 | 3 | 1 | 1 | 2 | 2 | 2 | 2
Mooring line breakage[8] | Manufacturing | Mooring line strength decrease or broken | 2 | 2.4 | 4 | 27.6 | 0.5 | Mooring lines | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 4 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Mooring line breakage[8] | Environmental condition | Mooring line strength decrease or broken | 2 | 2.4 | 3.5 | 24.8 | 0.5 | Mooring lines | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Mooring line breakage[8] | Environmental condition | Mooring line strength decrease or broken | 2 | 2.4 | 3.5 | 24 | 0.5 | Mooring lines | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Mooring Line Corrosion [1] | Maintenance | Mooring line strength decrease or broken | 3 | 2.4 | 3.5 | 27.4 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Mooring Line Fatigue [1] | Maintenance | Mooring line strength decrease or broken | 3.5 | 2.5 | 3.5 | 29 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 4 | 2 | 1 | 3 | 3 | 3 | 4
Mooring Line Fatigue [1] | Operation | Mooring line strength decrease or broken | 3.5 | 2.5 | 3.5 | 31 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 4 | 2 | 1 | 3 | 3 | 3 | 4
Mooring line wear [1] | Manufacturing | Mooring line strength decrease or broken | 3 | 2.5 | 4 | 35.6 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 4 | 1 | 3 | 2 | 1 | 3 | 3 | 3 | 4
Mooring line wear [1] | Design | Mooring line strength decrease or broken | 2 | 2.5 | 4 | 25.8 | 0.5 | Mooring lines | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 4 | 1 | 2 | 2 | 1 | 3 | 3 | 3 | 4
Mooring line wear [1] | Operation | Mooring line strength decrease or broken | 3 | 2.5 | 3.5 | 35.2 | 0.5 | Mooring lines | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 3 | 2 | 1 | 3 | 3 | 3 | 4
Mooring lines broken [1,3] | Operation | Asset not in correct location or position | 3 | 2.5 | 3.5 | 28 | 1 | Mooring lines | 1 | 2 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 4 | 2 | 1 | 3 | 3 | 3 | 4
Mooring lines broken [1,3] | Maintenance | Asset not in correct location or position | 2 | 2.5 | 3.5 | 18.4 | 1 | Mooring lines | 1 | 2 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 2 | 2 | 1 | 3 | 3 | 3 | 4
Mooring lines broken [1,3] | Operation | Asset not in correct location or position | 2.5 | 2.5 | 3.5 | 28.8 | 1 | Mooring lines | 1 | 2 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 3 | 2 | 1 | 3 | 3 | 3 | 4
Mooring lines broken [1,3] | Operation | Asset not in correct location or position | 2 | 2.5 | 3.5 | 34.8 | 1 | Mooring lines | 1 | 2 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 2 | 2 | 1 | 3 | 3 | 3 | 4
Mooring winch failure [1] | Design | Asset not in correct location or position | 2 | 2.5 | 4 | 24.8 | 1 | Mooring lines | 1 | 2 | 1 | 1 | 4 | 3 | 4 | 4 | 1 | 2 | 2 | 1 | 3 | 3 | 3 | 4
Mooring winch failure [1] | Maintenance | Asset not in correct location or position | 2 | 2.5 | 4 | 26.4 | 0.5 | Mooring lines | 1 | 2 | 1 | 1 | 4 | 3 | 4 | 4 | 0 | 2 | 2 | 1 | 3 | 3 | 3 | 4
accelerated mechanical fatigue | Design | Cable weakening | 3 | 2.9 | 3 | 32 | 1 | Dynamic cable | 1 | 2 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 4 | 2 | 1 | 3 | 4 | 4 | 2
anchoring damages | Environmental condition | Cables stress | 2 | 2.6 | 2.5 | 20 | 0 | Dynamic cable | 0 | 2 | 1 | 2 | 4 | 4 | 4 | 4 | 0 | 2 | 1 | 1 | 1 | 4 | 4 | 1
Cable Damage | Operation | Operational disruption | 3 | 2.9 | 3 | 32 | 1 | Dynamic cable | 1 | 2 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 4 | 2 | 1 | 4 | 4 | 4 | 2
Corrosion of J-tube [6] | Installation | J-tube degradation affecting cable integrity | 3 | 2.4 | 3 | 27 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 3 | 1 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 4 | 4 | 3
Corrosion of J-tube [6] | Design | J-tube degradation affecting cable integrity | 2.5 | 3.1 | 3.5 | 26.75 | 1 | Dynamic cable | 1 | 2 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 3
Crushing or deformation | Design | Cable weakening | 2 | 2.9 | 3 | 24 | 0.5 | Dynamic cable | 0 | 2 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 2 | 2 | 1 | 3 | 4 | 4 | 2
damage and corrosion of mechanical parts | Design | Total loss of the line | 2 | 2.9 | 3 | 24 | 1 | Dynamic cable | 1 | 2 | 1 | 1 | 4 | 4 | 4 | 3 | 1 | 2 | 2 | 1 | 4 | 4 | 4 | 3
Debris disturbance | Environmental condition | Power disruption | 2.5 | 2.9 | 2.5 | 21 | 0.5 | Dynamic cable | 1 | 3 | 1 | 2 | 4 | 4 | 4 | 3 | 0 | 2 | 2 | 1 | 3 | 4 | 4 | 2
Detachment | Operation | Water penetration | 3 | 2.9 | 2.5 | 24.25 | 1 | Dynamic cable | 1 | 3 | 1 | 2 | 4 | 4 | 4 | 3 | 1 | 3 | 2 | 1 | 3 | 4 | 4 | 2
Failure of end termination [6] | Manufacturing | breakdown of insulation | 3 | 2.4 | 3 | 28.5 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 3 | 3 | 1 | 4 | 4 | 4 | 3
Failure of end termination [6] | Manufacturing | breakdown of insulation | 3 | 2.6 | 3 | 30.75 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 3 | 3 | 1 | 4 | 5 | 5 | 3
Failure of end termination [6] | Manufacturing | breakdown of insulation | 3 | 2.3 | 3 | 28.5 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 3 | 3 | 1 | 3 | 4 | 4 | 3
Failure of fixing clamps | Operation | Exposure to elements | 3 | 2.9 | 2.5 | 31 | 0.5 | Dynamic cable | 0 | 3 | 1 | 2 | 4 | 4 | 4 | 3 | 1 | 3 | 2 | 1 | 3 | 4 | 4 | 2
Failure of insulations | Design | Power disruption | 2.5 | 3.3 | 3 | 29.5 | 1 | Dynamic cable | 1 | 2 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 3 | 2 | 1 | 5 | 5 | 5 | 2
Failure of sheath | Operation | Exposure to elements | 3 | 3 | 4 | 37 | 0 | Dynamic cable | 0 | 3 | 1 | 2 | 4 | 4 | 4 | 4 | 0 | 3 | 3 | 1 | 3 | 4 | 4 | 4
Failure of watertightness | Manufacturing | Power disruption | 2.5 | 3.3 | 3 | 32.75 | 1 | Dynamic cable | 1 | 2 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 3 | 2 | 1 | 5 | 5 | 5 | 2
Failure of watertightness | Operation | Power disruption | 2.5 | 3.3 | 3 | 28.5 | 1 | Dynamic cable | 1 | 3 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 2 | 2 | 1 | 5 | 5 | 5 | 2
failures of conductors | Operation | Loss of production | 3 | 3 | 2.5 | 30 | 1 | Dynamic cable | 1 | 3 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 3 | 2 | 1 | 4 | 4 | 4 | 1
Fatigue Cracks | Operation | Cable weakening | 2.5 | 3 | 3.5 | 42 | 1 | Dynamic cable | 1 | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 1 | 4 | 2 | 1 | 4 | 4 | 4 | 3
Geo-Hazards | Design | Power disruption | 1.5 | 3.6 | 2.5 | 20.6667 | 1 | Dynamic cable | 1 | 1 | 2 | 2 | 5 | 4 | 5 | 4 | 1 | 2 | 2 | 1 | 5 | 5 | 5 | 1
Loss of dynamic positioning | Environmental condition | Cables stress | 3.5 | 2.8 | 3 | 28.5 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 4 | 1 | 4 | 2 | 1 | 4 | 4 | 4 | 2
Loss of float bility (water adsorption) | <None> |  | 2.5 | 2.5 | 3 | 24 | 0 | Dynamic cable | 0 | 2 | 1 | 1 | 2 | 3 | 3 | 4 | 0 | 3 | 2 | 1 | 4 | 4 | 4 | 2
material degradation | Design | Loss of production | 2.5 | 2.9 | 2.5 | 17.25 | 1 | Dynamic cable | 1 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 4 | 2 | 1 | 4 | 4 | 4 | 1
Mechanical degradation [20] | <None> |  | 2 | 2.5 | 2.5 | 12.3333 | 1 | Dynamic cable | 1 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 1
Movement of CPS due to scour/seabed mobility [6] | Design | Cable being vulnerable to scour and need for repair or replacement | 1.5 | 2.5 | 4 | 28 | 0.5 | Dynamic cable | 0 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Movement of CPS due to scour/seabed mobility [6] | Design | Cable being vulnerable to scour and need for repair or replacement | 2 | 2.5 | 4 | 30.6667 | 0.5 | Dynamic cable | 0 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Movement of CPS due to scour/seabed mobility [6] | Installation | Cable being vulnerable to scour and need for repair or replacement | 3 | 2.5 | 4 | 41.3333 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 4 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Premature damage of outer protection layer | Environmental condition | Exposure to elements | 2.5 | 2.5 | 3 | 28.6667 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 3 | 1 | 2 | 1 | 1 | 3 | 3 | 3 | 3
Reduced sediment cover lower than designed value for protection [6] | Design | Replacement of cable | 2 | 2.8 | 3.5 | 29.75 | 1 | Dynamic cable | 1 | 1 | 1 | 2 | 5 | 5 | 5 | 4 | 1 | 3 | 1 | 1 | 3 | 2 | 3 | 3
Reduced sediment cover lower than designed value for protection [6] | Design | Replacement of cable | 2 | 2.8 | 3.5 | 23.5 | 1 | Dynamic cable | 1 | 1 | 1 | 2 | 5 | 5 | 5 | 4 | 1 | 3 | 1 | 1 | 3 | 2 | 3 | 3
Reduced sediment cover lower than designed value for protection [6] | Environmental condition | Replacement of cable | 2.5 | 2.8 | 3.5 | 32 | 1 | Dynamic cable | 1 | 1 | 1 | 2 | 5 | 5 | 5 | 4 | 1 | 4 | 1 | 1 | 3 | 2 | 3 | 3
Small bending radius | Operation | Insulation degradation | 3 | 2.4 | 3 | 31.75 | 0.5 | Dynamic cable | 0 | 3 | 1 | 1 | 4 | 3 | 4 | 3 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 3
Abnormal vibration | Design | Excessive Fatigue Life Consumption | 3 | 3 | 3 | 28 | 0 | Tower | 0 | 4 | 3 | 5 | 5 | 1 | 5 | 2 | 0 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Abnormal vibration | Environmental condition | Excessive Fatigue Life Consumption | 3 | 3 | 3 | 28 | 0 | Tower | 0 | 4 | 3 | 5 | 5 | 1 | 5 | 2 | 0 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Abnormal vibration | Installation | Potential collapse | 2 | 3.4 | 3.5 | 23.25 | 0 | Tower | 0 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Abnormal vibration | Maintenance | Potential collapse | 2 | 3.9 | 3.5 | 23.5 | 0 | Tower | 0 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Environmental condition | Failure of whole facility and vast economic loses | 2 | 2.8 | 4 | 18.2 | 0.5 | Tower | 0 | 2 | 1 | 2 | 2 | 2 | 2 | 5 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Environmental condition | Failure of whole facility and vast economic loses | 3 | 4.1 | 3.5 | 34.4 | 1 | Tower | 1 | 4 | 5 | 4 | 4 | 4 | 5 | 4 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Environmental condition | Potential collapse | 3 | 4.1 | 3.5 | 36.4 | 0.5 | Tower | 1 | 4 | 5 | 4 | 4 | 4 | 5 | 4 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Design | Potential collapse | 1 | 1.9 | 2 | 27.3333 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Tower Cracks | Manufacturing | Potential collapse | 1 | 1.9 | 2 | 40 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Tower Cracks | Fabrication | Potential collapse | 1 | 1.9 | 2 | 27.3333 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Tower Cracks | Fabrication | Potential collapse | 1 | 1.9 | 2 | 27.3333 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Tower Cracks | Installation | Potential collapse | 2.5 | 3.9 | 4.5 | 36.25 | 0 | Tower | 0 | 3 | 4 | 4 | 4 | 4 | 4 | 5 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Tower Cracks | Maintenance | Potential collapse | 1.5 | 1.9 | 1.5 | 27 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Operation | Potential collapse | 1.5 | 1.9 | 1.5 | 21.6667 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Maintenance | Potential collapse | 1.5 | 1.9 | 1.5 | 25 | 0 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 2 | 5 | 5 | 5 | 3
Tower Cracks | Design | Failure of whole facility and vast economic loses | 0.5 | 1.7 | 2 | 15.3333 | 0.5 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 5 | 5 | 5 | 4
Tower Cracks | Environmental condition | Failure of the WTG/Major repair campaign/Structure reassessment | 3 | 3.4 | 4 | 33.5 | 0.5 | Tower | 0 | 4 | 2 | 3 | 4 | 4 | 4 | 4 | 1 | 2 | 1 | 1 | 5 | 5 | 5 | 4
Tower Cracks | Design | Failure of whole facility and vast economic loses | 3 | 3.4 | 3.5 | 31 | 0.5 | Tower | 0 | 4 | 2 | 3 | 4 | 4 | 4 | 3 | 1 | 2 | 1 | 1 | 5 | 5 | 5 | 4
Tower Cracks | Manufacturing | Failure of whole facility and vast economic loses | 0.5 | 1.7 | 2 | 18.6667 | 0.5 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 5 | 5 | 5 | 4
Tower Cracks | Maintenance | Failure of whole facility and vast economic loses | 1 | 1.7 | 2 | 20.6667 | 0.5 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 1 | 5 | 5 | 5 | 4
Tower Cracks | Operation | Failure of whole facility and vast economic loses | 1 | 1.7 | 2 | 18.6667 | 0.5 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 1 | 5 | 5 | 5 | 4
Plastic deformation | Manufacturing | Potential collapse | 2.5 | 3.5 | 3 | 23.5 | 0 | Tower | 0 | 3 | 2 | 3 | 3 | 4 | 4 | 2 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Plastic deformation | Design | Potential collapse | 2 | 3.9 | 3 | 24.4 | 0.5 | Tower | 1 | 2 | 2 | 4 | 5 | 4 | 5 | 2 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Tower collapse | Operation | Failure of whole facility and vast economic loses | 0.5 | 1.9 | 2 | 22 | 0.5 | Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 5 | 5 | 5 | 4
Transition piece break | Design | Tower Unit collapse, Floater Unit damage | 2.5 | 4 | 3.5 | 35.25 | 1 | Transition piece | 1 | 3 | 3 | 4 | 5 | 4 | 5 | 3 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Transition piece break | Operation and Maintenance | tension failure (rupture), buckling of the transition piece/ Tower unit damage | 2.5 | 3.4 | 3.5 | 30.25 | 0.5 | Transition piece | 1 | 3 | 3 | 4 | 5 | 4 | 5 | 3 | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 4
Structural plastic deformation | Operation | Local stress accumulation | 2.5 | 2.8 | 3.5 | 29 | 0.5 | Transition piece | 1 | 3 | 3 | 3 | 4 | 3 | 4 | 3 | 0 | 2 | 1 | 1 | 3 | 3 | 3 | 4
Transition Piece Cracks | Operation | Tower transition piece connections failure / resonance | 3 | 3 | 4 | 36.5 | 0.5 | Transition piece | 1 | 4 | 2 | 4 | 4 | 3 | 4 | 5 | 0 | 2 | 1 | 1 | 4 | 3 | 4 | 3
Transition piece break | Environmental condition | Tower Unit collapse, Floater Unit damage | 0.5 | 1.9 | 2 | 21.6667 | 0.5 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 5 | 5 | 5 | 4
Transition piece vibration | Operation | potential tower connections failure | 3 | 3.6 | 4 | 38 | 0 | Transition piece | 0 | 4 | 3 | 4 | 5 | 5 | 5 | 4 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Structural plastic deformation | Installation | Local stress accumulation | 1.5 | 1.4 | 1.5 | 26.6667 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 3
Transition Piece Cracks | Installation | Tower transition piece connections failure / resonance | 3 | 3.6 | 3.5 | 33 | 0 | Transition piece | 0 | 3 | 3 | 4 | 5 | 5 | 5 | 4 | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 3
Transition Piece Cracks | Environmental condition | Tower transition piece connections failure / resonance | 2.5 | 3.7 | 4 | 32 | 0.5 | Transition piece | 1 | 3 | 3 | 5 | 5 | 5 | 5 | 4 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Transition Piece Cracks | Fabrication | potential tower connections failure | 1.5 | 1.4 | 2 | 26 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 4
Transition piece vibration | Maintenance | potential tower connections failure | 1 | 1.4 | 2 | 24 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Structural plastic deformation | Maintenance | Local stress accumulation | 1.5 | 1.1 | 2 | 24.6667 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 3 | 3 | 3 | 4
Transition Piece Cracks | Maintenance | Tower transition piece connections failure / resonance | 3 | 2.6 | 3 | 26 | 0 | Transition piece | 0 | 4 | 3 | 2 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 3
Transition Piece Cracks | Maintenance | Tower transition piece connections failure / resonance | 1 | 1.4 | 2 | 24.6667 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Transition Piece Cracks | Installation | Tower transition piece connections failure / resonance | 1.5 | 1.4 | 2 | 28 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 4
Transition piece break | Design | Tower Unit collapse, Floater Unit damage | 1 | 1.9 | 2 | 23.3333 | 0.5 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 4
Transition piece break | Operation and Maintenance | Tower Unit collapse, Floater Unit damage | 0.5 | 1.9 | 2 | 24 | 0.5 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 5 | 5 | 5 | 4
Transition Piece Cracks | Fabrication | Tower transition piece connections failure / resonance | 1 | 1.4 | 2 | 24.6667 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Transition Piece Cracks | Maintenance | Tower transition piece connections failure / resonance | 2.5 | 3.5 | 4.5 | 37.5 | 0 | Transition piece | 0 | 3 | 2 | 4 | 5 | 5 | 5 | 5 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Transition Piece Cracks | Maintenance | Tower transition piece connections failure / resonance | 1 | 1.4 | 2 | 25.6667 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 4 | 4 | 4 | 4
Transition Piece Cracks | Installation | Tower transition piece connections failure / resonance | 1.5 | 1.4 | 2 | 31 | 0 | Transition piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 4 | 4 | 4 | 4